## Slide 1: A Novel Hybrid Modeling Method for Predicting Energy Use of Hydronic Radiant Slab Systems
Lichen WU1, Liping WANG1, James BRAUN2
1Department of Civil and Architectural Engineering, University of Wyoming, Laramie, WY, 82071, United States
2School of Mechanical Engineering, Purdue University, West Lafayette, IN 47907-2088, United States

## Slide 2: Energy loads calculation
where is the supply and return water temperature; is the specific heat capacity; is density; is the flow volume rate.
Challenge
  radiant slab systems large thermal capacitance
Notes: equation
Radiant slab (concrete, pipe, chilled/water)/ thermal insulation
profile
Existing methods

## Slide 3: Building performance models
White box:
Finite difference
Black box:
Neural network;
(Growing) Gaussian Mixture Regression
Gray box:
Resistor-Capacitor (RC)
This study: RC+GGMR
Notes: Absolute physical

## Slide 4: Resistor Capacitor network introduction
RC
  Developing (flexible)
  Predict (warm-up time steps)
    State variables randomly initialized
    Recursive prediction
Braun, James E., and Nitin Chaturvedi. 2002. “An Inverse Gray-Box Model for Transient Building Load Prediction.” HVAC&R Research 8(1): 73–99.
State variables:
Input variables:
Output variables:
: resistances, capacitances and heat flux coefficients
Notes: Output variable (Energy), State variables (Troom), Input variables (Disturbance), Abcd (RC, coefficients).
Takeaway:
1. The training purpose is to ABCD;
2. Flexible choices for state variables (how many states will be used to represent the radiant slab?)

## Slide 5: RC model prediction needs warm up
RC
  Developing (flexible)
  Predict (warm-up time steps)
    State variables randomly initialized
    Recursive prediction
Notes: c, d, input, state
State is updated with older states
Random initialized
Chaotic <- prediction is not stable
Warm up period is needed. Statistically (input, stable state, Abcd -> determine prediction)

## Slide 6: RC models development 1/3
Notes: Radiant system (concrete, pipes, water inside the pipes)

## Slide 7: RC models development 2/3

## Slide 8: RC models development 3/3

## Slide 9: RC models performance

## Slide 10: Gaussian Mixture Regression introduction
GMR
O.rka. (2021, March 31). How to evaluate the loss on a Gaussian Mixture Model? [Forum post]. Cross Validated. https://stats.stackexchange.com/q/517652
Notes: Gaussian -> components (multivariate gaussian (mu, mean; sigma, covariance))
The sum over different components
Weighting coefficients
(mu, covariance -> determine prediction) (working condition is change over time, update mechanism)

## Slide 11: Growing GMR introduction
New
Data
New
Component
Components
update
Components
update
Components
…
GMR
New
Data
New
Component
GMR
Li, Deyang, and Zhihuan Song. 2020. “A Novel Incremental Gaussian Mixture Regression and Its Application for Time-Varying Multimodal Process Quality Prediction.” In 2020 IEEE 9th Data Driven Control and Learning Systems Conference (DDCLS), , 645–50.
Bouchachia, Hamid, and Charlie Vanaret. 2011. “Incremental Learning Based on Growing Gaussian Mixture Models.”
Notes: New inputs;
Learning rate
Older version -> newer version
Guidance (as accurate as possible) needed for GGMR
RC prediction

## Slide 12: The Novel Hybrid Approach
Hybrid approach
  RC + GGMR
    Warm-up time steps
    Complexities
GGMR
Module
Current timestamp,
input
RC model
warming up
RC model prediction
RC predicted load at timestamp j,
RC Module
input
Notes: Workflow:
Current -> RC starts warming up from 14 time steps ago
RC prediction -> Update the historical components

## Slide 13: Metrics
Absolute error
  Mean absolute errors (MAE)
Relative percentage errors
  RMSE (NRMSE, CVRMSE)
  Mean absolute percentage error
Notes: Absolute error/ Relative error
1. Coefficient of variation; The ASHRAE Guideline 14, hourly should be below 30%
2. MAPE (absolute energy consumption)

## Slide 14: Performance
Notes: Measurement;
RC, GGMR (No RC prediction), Hybrid (With RC prediction available)
When get the prediction from RC, it become Hybrid, the best performance.

## Slide 15: Performance
Notes: 6.43 CVRMSE (Much lower than 30%)

## Slide 16: Conclusions
In the current study, from the comparison of the Resistor Capacitor network, GGMR, and the hybrid approach:
RC model has better explainability, prediction than GGMR.
GGMR is easier to get constructed and trained than RC model.
The hybrid approach (RC+GGMR) has the best prediction performance among these approaches.

## Slide 17: Q&A
Thank you!

## Slide 18: Possible Questions
Q
Why GGMR is necessary?
Why RC is necessary?
Why hybrid is necessary?
Have you tried other features for GGMR?
What’s the input variables (can be predicted?)
GGMR update rules
Performance explanation
A
RC: 𝑇𝑜𝑢𝑡,𝑇𝑠𝑙𝑎𝑏1,𝑇𝑐𝑎𝑣,𝑇𝑠𝑜𝑢𝑟𝑐𝑒,𝑄̇𝑠𝑜𝑙,𝑄̇𝑖𝑛𝑡,𝑄̇𝑙𝑖𝑔ℎ𝑡,𝑄̇𝐴𝐻𝑈,𝑑𝑇𝑠𝑜𝑢𝑟𝑐𝑒/𝑑𝑡
GGMR: 𝑇𝑜𝑢𝑡,𝑇𝑠𝑙𝑎𝑏𝑠,𝑇𝑐𝑎𝑣,𝑉𝑎𝑙𝑣𝑒𝑐𝑙,𝑉𝑎𝑙𝑣𝑒ℎ𝑡,𝐹𝑙𝑜𝑤𝑃𝑟𝑒𝑑𝑖𝑐𝑡𝑒𝑑,𝐺𝐺𝑀𝑅
Hybrid:
𝑇𝑜𝑢𝑡,𝑇𝑠𝑙𝑎𝑏𝑠,𝑇𝑐𝑎𝑣,𝑉𝑎𝑙𝑣𝑒𝑐𝑙,𝑉𝑎𝑙𝑣𝑒ℎ𝑡, 𝐹𝑙𝑜𝑤𝑃𝑟𝑒𝑑𝑖𝑐𝑡𝑒𝑑,𝐺𝐺𝑀𝑅,𝑅𝐶𝑝𝑟𝑒𝑑𝑖𝑐𝑡𝑒𝑑,𝑅𝑒𝑎𝑙𝑇𝑖𝑚𝑒
Notes: RC: [𝑇𝑜𝑢𝑡,𝑇𝑠𝑙𝑎𝑏1,𝑇𝑐𝑎𝑣,𝑇𝑠𝑜𝑢𝑟𝑐𝑒,𝑄̇𝑠𝑜𝑙,𝑄̇𝑖𝑛𝑡,𝑄̇𝑙𝑖𝑔ℎ𝑡,𝑄̇𝐴𝐻𝑈,𝑑𝑇𝑠𝑜𝑢𝑟𝑐𝑒/𝑑𝑡]
GGMR: 𝑇𝑜𝑢𝑡,𝑇𝑠𝑙𝑎𝑏𝑠,𝑇𝑐𝑎𝑣,𝑉𝑎𝑙𝑣𝑒𝑐𝑙,𝑉𝑎𝑙𝑣𝑒ℎ𝑡,𝐹𝑙𝑜𝑤𝑃𝑟𝑒𝑑𝑖𝑐𝑡𝑒𝑑,𝐺𝐺𝑀𝑅
Hybrid: 𝑇𝑜𝑢𝑡,𝑇𝑠𝑙𝑎𝑏𝑠,𝑇𝑐𝑎𝑣,𝑉𝑎𝑙𝑣𝑒𝑐𝑙,𝑉𝑎𝑙𝑣𝑒ℎ𝑡, 𝐹𝑙𝑜𝑤𝑃𝑟𝑒𝑑𝑖𝑐𝑡𝑒𝑑,𝐺𝐺𝑀𝑅,𝑅𝐶𝑝𝑟𝑒𝑑𝑖𝑐𝑡𝑒𝑑,𝑅𝑒𝑎𝑙𝑇𝑖𝑚𝑒

## Slide 19: GGMR-Update Rules

## Slide 20: Hourly Performance Explanation
Scenario 1,
Scenario 2,